Division(s):

ITEM CA17

CABINET – 19 SEPTEMBER 2006

FIRE PRECAUTIONS ON SCHOOL PREMISES

Report by Director for Community Safety & Chief Fire Officer

Introduction

- The Council on 20 June 2006 adopted the following motion which has been referred to the Cabinet for consideration:

“Council is very concerned at the recent spate of arson attacks on school premises in Oxfordshire. The damage to premises is disruptive and costly, the damage to children’s school work and text books seriously demoralising and the effect on the teaching and learning environment of teachers and children extremely damaging.

Council recognises that an early warning of fire is essential in ensuring that any damage to the structure of the school is kept to a minimum, and that the provision of a fire alarm system with automatic fire detection linked to the Fire and Rescue Service is the best way to achieve this. With the increasing threat of arson to our schools, we should investigate and progress all cost effective solutions to protect them and the provision of sprinklers in schools would ensure that any fires started would be kept under control until the arrival of the Fire and Rescue Service.

Council therefore asks the Cabinet to:

(a) 	encourage all schools in Oxfordshire to fit automatic fire alarms linked to the Fire and Rescue Service and in new schemes to do so in accordance with the agreed risk assessment process;

(b) 	recommend that all new schools, and extensions or major refurbishments to existing schools, be fitted with sprinklers when the agreed risk assessment process demonstrates its efficacy.”

- A full briefing note on sprinklers in schools with fire losses incurred by the Council is attached at Annex 1.

Approach to fire safety in schools

- Property Services and the Fire and Rescue Service agree with the risk assessment approach to fire safety in schools and will jointly, if agreed by Cabinet, carry out the following actions:

- Review the current Fire Safety Strategy for all County Council buildings.

- As part of the Fire Safety Strategy develop a “Fire Suppression and Alarm Systems Risk Assessment” sheet. This will require that a risk assessment is carried out in the very early design stages of a project to determine whether sprinklers would be appropriate and the level of fire alarm and detection systems required. The risk assessment process would take into account such issues as the social and economic consequences of a fire for both students and the wider community, storage of materials, public access to the site, vulnerability of the construction to fire, security measures at the site, history of vandalism and arson, local socio-demographic factors, access for the Fire and Rescue Service.

- In consultation with the Director for Children, Young People & Families, provide guidance to schools recommending the use of the Fire Safety Strategy when carrying out new building projects using self finance or devolved capital funding. The guidance will also include a recommendation that schools review their current fire alarm and detection systems in existing buildings and to consider using delegated funding to fit an automatic link to an alarm receiving centre which alerts the Fire and Rescue Service.

- Establish a working group involving Property Services, the Fire and Rescue Service, Children, Young People & Families and the County Council’s insurers to agree the standard of sprinkler installation where the risk assessment process indicates that sprinklers are required in schools and to investigate the use of mist systems in the protection of high risk areas and life safety issues.

Financial and Staff Implications

- The cost of sprinklers will need to be incorporated into the design of school premises, which may lead to increased capital expenditure on school projects, where there will limited increased revenue costs for maintenance. This needs to be considered against reduced expenditure on insurance premiums and the cost of recovering building stock after an incident.

RECOMMENDATION

- The Cabinet is RECOMMENDED to agree the actions set out in Paragraph 5 above.

JOHN PARRY

Director for Community Safety & Chief Fire Officer

Contact Officer: Mike Smyth, Deputy Chief Fire Officer, Tel: 01865 855 205

Background papers:	 Nil

September 2006

ANNEX 1

BRIEFING NOTE: SPRINKLERS IN SCHOOLS

AUGUST 2006

## Background

- Oxfordshire Fire & Rescue Service, as fire professionals have been convinced of the effectiveness of sprinkler systems in controlling and extinguishing fires for some considerable time.

“Given that 75% of educational establishments’ fires are caused by arson attacks and the tremendous costs associated with the losses. Not one of the schools in 2005 (nationally) that suffered a large fire was fitted with a sprinkler system, it seems entirely appropriate that ALL new build schools (and major refurbishments) be fitted with sprinklers as a matter of course”. (Zurich Municipal)

- In the USA, following a number of multi-facility school fires in the late 1950s, the approved building codes were changed to install sprinklers in the majority of their schools. With five times the numbers of schools compared to the UK, they have an annual fire loss of approximately £50 million (UK £106 million in 2004. Comparing like with like, the figures would be £50 million (USA) to £530 million in the UK).

“There are an increasing number of fires in schools which are now occurring during the daytime raising the potential of injury should children/staff become trapped in burning buildings”. (Zurich Municipal)

- The Government is currently embarked on the ‘Building Schools or the Future’ (BSF) project involving huge outlay for the next 10-15 years. Given that the most appropriate and cost effective time to fit sprinklers to schools is during the building process this would appear to be an ideal opportunity to invest to protect Oxfordshire’s schools.

- The success of the BSF Programme is directly linked to this issue of fire safety.  Every year around 2,000 schools in Britain are damaged by fire.   For a school to be environmentally, economically and socially sustainable, any risk of potential structural damage must be minimised.   Working towards guaranteeing the longevity of the school building will ensure that the premises can “meet the needs of the present without compromising the ability of future generations to meet their own needs”.

- The British Automatic Fire Sprinkler Association has just launched a new campaign entitled 'Wise up to Fire' in which they aim to make society aware of the potential benefits regarding the of fitting sprinklers in schools.

#### The Current Legislative & Regulatory Situation

- Currently there is no legislative requirement for the mandatory fitting of sprinklers in school buildings. All school buildings must comply with Approved Document B (Fire Safety) of the Building Regulations. These regulations, which are the responsibility of the Department for Communities and Local Government (DCLG), do not require schools to install sprinkler systems, but do not preclude Local Education Authorities from doing so.

- The installation of sprinklers is dealt with in Building Bulletin 100, Designing and Managing Against the Risk of Fire in Schools. This is non-statutory guidance published by the Department for Education and Skills (DfES).

- As both the DfES and the DCLG are involved in the fire regulations and guidance relating to schools, there has been some confusion as to which department has the lead on developing Building Bulletin 100.  However, former Fire and Rescue Services Minister, Jim Fitzpatrick MP, recently clarified the situation:

“The Department for Education and Skills is in the lead in considering Building Bulletin 100 and a revision of the provision of sprinklers in schools. Its consultation will conclude later this year, and we are looking forward to that to find out whether we can move forward on this very important issue.” Jim Fitzpatrick MP, previous Fire and Rescue Service Minister, in response to Oral Question (Hansard, Column 106,19 April 2006)

- After many months of indicating that a reviewed version of Building Bulletin 100 (BB100) would be published, a draft version of the guidance finally underwent consultation, which closed on 18 November 2005.  The version of the guidance that was put out for consultation stated that a risk assessment should be undertaken before any decision was made as to the provision of sprinklers in schools.

- The DfES has yet to publish an analysis of responses to the consultation, or a revised version of the guidance, however the Schools Minister Jim Knight MP recently indicated that the analysis had been completed and would be published shortly. It is expected that a new section will be inserted into BB100 detailing the design parameters for sprinklers in schools. The Department hopes to publish the final, revised version of the guidance before the end of this year (06).

- Since the consultation concluded, the DfES has continued to indicate its support for using risk assessment and cost benefit analysis to determine whether to install sprinklers in schools.  For example, Schools Minister, Jim Knight MP, gave the following response to a Written Question from Joan Walley MP:

“We work closely with colleagues in the new Department for Communities and Local Government (DCLG) and, liaising with them, we produced new draft guidance on fire safety—Building Bulletin (BB) 100, “Designing and Managing Against the Risk of Fire in Schools”. It stresses the value of using risk assessments to determine what sort of fire detection and alarm systems should be used in each school, and whether or not sprinklers should be installed. While saying that a building designed in accordance with the guidance in Approved Document B (Fire Safety), which accompanies the Building Regulations, will achieve a satisfactory standard of life safety, it also suggests ways of improving property protection.”  (Hansard, Column 910, 16 May 2006).

- However, risk assessment or cost benefit analysis only predict the damage that would be caused by school fires in terms of the cost of material damage and the cost of the Fire and Rescue service attending the fire.  They do not reflect the damage and disruption suffered by a local community in the aftermath of a school fire, and can therefore never be accurate.

The Economic Case for Fitting Sprinklers

- The Government is investing £2.2 billion in the Building Schools for the Future (BSF) programme and over the next 10-15 years there will be further funds invested in this programme to upgrade or replace all secondary schools.

- Since the year 2000, over £500 million has been lost in school fire costs alone, nearly a quarter of the Government's start up funding. This is because sprinkler suppression systems are not a requirement of school building programmes despite being recognised as one of the most effective means of combating the risk of fire.

- There is currently much debate regarding the cost associated with the fitting of sprinklers. Government department quote 5% to 10% of total build cost for the installation of sprinklers. Zurich Municipal suggests that these figures are overstated.

In fact a sample of 21 recently designed schools (2004 onwards) of mixed construction, size and value, the average cost of the sprinkler installation is 1.98% (Zurich Municipal).

- Oxfordshire County Council (OCC) Insurers (Zurich Municipal) are now offering up to 75% reduction in fire insurance premiums if sprinklers are installed, and in addition will remove the mandatory excess, currently OCC excess is £200,000.

- The provision of sprinkler systems in a building allows greater flexibility in the building design with the effect of reducing costs.  Sprinklers can save on building costs because under the building regulations larger compartment sizes may be constructed. Reduced boundary and extended travel distance to fire exits are allowed.  A reduction in structural fire protection is also possible.

- In determining the exact figures on the cost of fires to schools is very difficult to ascertain.  It is estimated, based on insurance claims that the cost to schools in England and Wales stands in excess of £100 million per year.  The total year on year loss, if school fires continue to rise at the present rate, up until 2016 is estimated at £3 billion.  However, the true cost is likely to be significantly higher as insurance costs cannot reflect the level of disruption, social impact, environmental damage or the effect on learning that a fire causes.

- The cost of installing sprinkler protection to a new school is as little as 1.98% of the total building cost and it is estimated that even a retrofitted system will pay for itself in savings from fire damage within 8-11 years. The cost of installing a sprinkler system is roughly equivalent to carpeting the same building (Zurich Municipal)

#### The Environmental & Social Case for Fitting Of Sprinklers

- The economic loss does not take into account the effects on the environment due to pollutants from fire, smoke and water run off, or the social loss to local communities. This is particularly significant as the BSF programme aims to make school buildings more community friendly with extended opening hours for community activities to take place in them.

- Sprinklers reduce building damage and have the potential to increase the lifespan of a building.  Buildings that have a fire are usually uninhabitable afterwards and may have to be demolished.  However, a sprinkler protected room can usually be back in use within a few hours and the rest of the building is usually unaffected.

- Sprinklers help to protect the environment by controlling a fire in its early stages, preventing airborne pollution and water run-off. Sprinklers save water.  Statistics show that the widespread use of sprinklers could save up to 96% of the 5.6bn litres of water used annually in the UK to fight large school fires. Typically, the amount of water used to control a fire from a sprinkler system is only 5% of that used by a single fire service hose.

- However it not just the financial cost of school fire that should concern us. Loss of coursework causes considerable mental stress to pupils and may mean they are at a disadvantage when passing crucial exams. Moreover schools are now valuable facilities to the local community and their loss is felt far beyond the classroom.

- Stuart Blackie a risk management consultant for Zurich Municipal has offered to give a 10-15 minute presentation to councillors. Stuart was one of the authors of the CFOA guidance on the provision of sprinklers in schools and has written an article in the FPA regarding the “Design & Management of School Buildings”.

2004 UK School Fire

Total Fire loss £106,000,000

Fire & Rescue Service

August 2006